## Slide 1: Develop and Evaluate a Transferable Model Predictive Control Based Group Occupant-Centric Control Strategy
May 21, 2025
Yicheng Li

## Slide 2: Acknowledgments
Financial Support:
  U.S. Department of Energy via grant EE-0009153 (Hardware-in-the-loop Laboratory Performance Verification of Flexible Building Equipment in a Typical Commercial Building)
Committee Members:
  Jin Wen, PhD. (Drexel University)
  James Lo, PhD. (Drexel University)
  Simi Hoque, PhD. (Drexel University)
  Zhelun Chen, PhD. (Daikin Comfort)
  Amanda Pertzborn, PhD. (National Institute of Standards and Technology)

## Slide 3: Outline
Introduction
Research Objectives
Research Contents
  Task 1: Virtual Testbed Development
  Task 2: Predictive Model Development
  Task 3: Transfer Learning Used in Group Occupant Thermal Comfort Model
  Task 4: Development of MPC-based Group Occupant Centric Control
Conclusions and Future Works

## Slide 4: Introduction
People spend an average of 87% of their time indoors [1]
Indoor environmental quality (IEQ) issues can have a direct impact on occupant comfort, health and productivity
Traditional building system
Predefined schedule
Standardized comfort demand
Over-conditioning and waste of energy
Does not guarantee the comfort need of specific group of occupants
Building automation system
Machine Learning
Technological progress
[1] Klepeis, N.E., et al., The National Human Activity Pattern Survey (NHAPS): a resource for assessing exposure to environmental pollutants. Journal of Exposure Science & Environmental Epidemiology, 2011. 11(3): p. 231-252.
MPC-based Occupant-Centric Control (OCC)
Sensing
Prediction
Control
Building

## Slide 5: Research Gaps
The development of MPC-based OCC requires a comprehensive testbed, including occupants, HVAC system, and the building
  Data support
  Control evaluation
In reviewed OCC studies
  Experiment study: involve real occupant in a real building or conditioning chamber
    Non-repeatable
  Simulation study: use simulated HVAC system and occupant models
    Not publicly available
Gap 1: Not publicly available testbed to support the development of MPC-based OCC strategy
Key components needed in testbed
HVAC system
Occupant
Building

## Slide 6: Research Gaps
Emerging thermal comfort models
Individual thermal comfort model
Lead to comfort conflict in group occupants
Typical thermal comfort model
Used for general population, such as PMV
Deviated when used for specific occupants
In the prediction process, there are several predictive models
  One of them is occupant thermal comfort model
Gap 2: Lack of thermal comfort model for a specific groups of occupants
The general framework of OCC
Sensing
Prediction
Control
Building

## Slide 7: Research Gaps
In predictive model training, the occupant data collection is time-consuming
  Occupant work interruption
  Sensor fail
Due to the difference between occupant, one occupant thermal comfort model is different with another occupant thermal comfort model
Gap 3: Difficulty in collecting sufficient data to develop a thermal comfort model for a specific group of occupants
The general framework of OCC
Sensing
Prediction
Control
Building

## Slide 8: Research Gaps
The MPC optimizes building system control to
  Improve occupant thermal comfort
  Reduce energy consumption
The development of MPC-based OCC is challenging, especially when considering
  A specific group of occupants
The performance of the MPC-based OCC needs to be systematically evaluated
Gap 4: Lack of a systematic framework for MPC-based group OCC development and evaluation
The general framework of OCC
Sensing
Prediction
Control
Building

## Slide 9: Research Objectives
Objective 1
Develop a virtual testbed covering HVAC system, building, and the occupant components
Transferable MPC-based Group OCC
(TMPC-GOCC)
Objective 2
Develop a group occupant thermal comfort prediction model
Objective 3
Develop transfer learning method used for group occupant thermal comfort model
Objective 4
Develop and evaluate a transferable MPC-based group OCC strategy
Gap 1
No testbed
Gap 4
MPC-based group OCC
Gap 2
Comfort conflict
Gap 3
Insufficient data

## Slide 10: Overview of the Research
Objective 2
Objective 1
Objective 3
Objective 4

## Slide 11
Objective 1: Virtual Testbed Development
(Presented in thesis proposal)
Task 1.1 HVAC System Model
Task 1.2 Zone Model
Task 1.3 Occupant Thermal Comfort Model

## Slide 12: Overall Virtual Testbed Framework
The virtual testbed framework include:
  HVAC system model
  Zone model
  Occupant comfort model
  Supervisory control
Virtual testbed framework

## Slide 13: Overall Virtual Testbed Framework
Task 1.1 HVAC System Model
A two-stage Air Source Heat Pump (ASHP) at National Institute of Standards and Technology [1]
Virtual testbed framework
[1] Payne, W.V., S.H. Yoon, and P.A. Domanski, Heating mode performance measurements for a residential heat pump with single-faults imposed. 2017: US Department of Commerce, National Institute of Standards and Technology.

## Slide 14: Overall Virtual Testbed Framework
Task 1.2 Zone Model
A typical small office EnergyPlus model from the Commercial Prototype Building Models [1]
Virtual testbed framework
[1] U. S. DOE. Commercial Prototype Building Models. Available: https://www.energycodes.gov/development/commercial/prototype_models

## Slide 15: Overall Virtual Testbed Framework
Task 1.3 Occupant Thermal Comfort Model
Adapted from an agent-based occupant’s thermal comfort and behaviors model [1]
Simulate occupant thermal comfort only
Virtual testbed framework
[1] Langevin, J., J. Wen, and P.L. Gurian, Modeling thermal comfort holistically: Bayesian estimation of thermal sensation, acceptability, and preference distributions for office building occupants. Building and Environment, 2013. 69: p. 206-226

## Slide 16: Conclusions of Objective 1
Objective 1: Virtual Testbed Development
A virtual testbed is developed, which uses ASHP to serve a single zone in small office with virtual occupants
  The testbed is used to generate the datasets for the development of predictive model, transfer learning method, and the TMPC-GOCC strategy

## Slide 17
Objective 2: Predictive Model Development
Task 2.1 Group Occupant Thermal Comfort Model Development
(Presented in thesis proposal)
Task 2.2 Zone Environment and HVAC System Power Model Development

## Slide 18: Task 2.1 Group Thermal Comfort Model Development
Challenge
  Comfort conflict in groups of occupants
Solution
  Develop an indicator to represent the thermal comfort of a group, and optimize it to reduce comfort conflict
  Definition of group thermal comfort using inclusive and homogeneous methods
    Inclusive: Everyone's opinion can be reflected in the results
    Homogeneous: All group members are equally important
    Definition: A number of the occupants within the group who feel comfortable
    The group thermal comfort could be flexibly adjusted
      For example, if considering the needs of the vulnerable, more weight can be given

## Slide 19: Task 2.1 Group Thermal Comfort Model Development
Methodology of the group thermal comfort model development and evaluation
  Raw data
    Obtained from a hardware-in-the-loop load flexibility study [1]
    Include the occupant thermal comfort votes with HVAC system and environment measurement
  Feature selection
    Based on the literature review, three commonly available features are selected
  Model type determination
    Classification model (the number of occupants is an integer, discrete number)
  Candidate model structure
    Artificial Neural Networks (ANN)
    Support Vector Machines (SVM)
    Random Forest (RF)
    k-Nearest Neighbor (kNN)
[1] Jin Wen, Z.C., et al., (2023), Hardware-in-the-loop Laboratory Performance Verification of Flexible Building Equipment in a Typical Commercial Building: Performance of Heating, Ventilation, and Air Conditioning and Thermal Energy Storage Across the United States, National Institute of Standards and Technology, https://doi.org/10.18434/mds2-3058

## Slide 20: Task 2.1 Group Thermal Comfort Model Development
Methodology of the group thermal comfort model evaluation
  Typical index:
    Instance-based accuracy
    Fail to capture the stochastic nature of occupant thermal comfort
  Proposed index:
    Similarity measures, which uses Jensen–Shannon divergence (JSD) to evaluate the difference of the two distributions [1]
Where:
and are two probability distributions in the sample space ;
and are the probabilities of the element in and , respectively.
[1] Menéndez M L, Pardo J A, Pardo L, et al. The jensen-shannon divergence[J]. Journal of the Franklin Institute, 1997, 334(2): 307-318.
An example of JSD=0.044
An example of JSD=0.320

## Slide 21: Task 2.1 Group Thermal Comfort Model Development
  Process
    Divide the entire feature space into several subspaces
    Calculate the JSDi in each subspace
    Calculate the weighted average JSD ()
Weighted mean JSD calculation schema
Methodology of the group thermal comfort model evaluation

## Slide 22: Task 2.1 Group Thermal Comfort Model Development
Candidate model structure selection
  By using the as evaluation index and the 5-fold cross-validation method, the suitable model structure for the group thermal comfort model is selected
  The Random Forest model development and evaluation method will be consistently used in the following study.
5-fold cross-validation schema
Candidate learning algorithms | Cross-validation error ()
ANN | 0.314
SVM | 0.247
RF | 0.114
kNN | 0.190
Candidate learning algorithms | 
ANN | 0.314
SVM | 0.247
RF | 0.114
kNN | 0.190
Cross-validation results

## Slide 23: Task 2.2 Zone Environment and HVAC System Power Model Development
Goal:
  Develop three models to predict zone air temperature, zone air relative humidity, and HVAC system power in the future time (prediction timestep = 15 min), respectively
Data generation
  Use the developed virtual testbed (Atlanta Summer) to generate the model training and validation data
    Training data
      Use active learning [1] to generate the zone air temperature setpoint (65℉ ~ 85℉)
      Simulation period: 2 days
    Validation data
      Randomly generate the zone air temperature setpoint (65℉ ~ 85℉)
      Simulation period: 1day
[1] Zhang, L. and J. Wen, A systematic feature selection procedure for short-term data-driven building energy forecasting model development. Energy and Buildings, 2019. 183: p. 428-442

## Slide 24: Task 2.2 Zone Environment and HVAC System Power Model Development
Feature selection
  Based on the literature, manually select the commonly available features:
Candidate model structures
  Artificial Neural Network (ANN)
  Recurrent Neural Network (RNN)
  Multiple Linear Regression (MLR)
  Multivariate Adaptive Regression Splines (MARS)

## Slide 25: Task 2.2 Zone Environment and HVAC System Power Model Development
Validation goal
  Determine model structure
  Determine the prediction horizon for MPC
Validation index
  Root Mean Square Error (RMSE):
Validation results
Candidate learning algorithms | Candidate Prediction Horizons (PH) |  |  | 
 | ph=1 | ph=2 | ph=4 | ph=8
ANN | 1.48 | 3.26 | 5.73 | 8.59
RNN | 3.47 | 5.82 | 8.36 | 11.09
MLR | 5.63 | 9.27 | 13.58 | 18.94
MARS | 1.51 | 2.74 | 4.74 | 8.12
Summary of validation error [%] in zone air relative humidity model
Zone air relative humidity MARS model validation results

## Slide 26: Task 2.2 Zone Environment and HVAC System Power Model Development
Validation results
  Model structures selection and error
    Zone air temperature RNN model: 0.21 °C
    Zone air relative humidity MARS model: 4.74%
    HVAC system power ANN model: 71W
  Prediction horizon (PH) selection
    PH=4, based on the typical criteria (0.5 °C for temperature, 5% for relative humidity, and 90W for HVAC system power [1])
[1] American Society of Heating, V., and Air Conditioning Engineers (ASHRAE), Guideline 14-2014, in Measurement of Energy and Demand Savings. 2014.

## Slide 27: Conclusions of Objective 2
Objective 2: Predictive Model Development
The definition of group thermal comfort was proposed, and the methodology for model training and validation was established (task 2.1)
  Selected model structures: Random Forest model
  Evaluation index:
The zone air temperature model, zone air relative humidity model, and HVAC system power model are developed (task 2.2)

## Slide 28
Objective 3: Transfer Learning (TL) Used in Group Occupant Thermal Comfort Model
Task 3.1 TL Framework Development
(Presented in thesis proposal)
Task 3.2 Evaluation Scenarios Design
Task 3.3 Evaluation Results Analyze

## Slide 29: Task 3.1 Transfer Learning Framework Development
Background
  A reliable group thermal comfort model need sufficient data to train
  The data collection of occupant is time-consuming
  There is often a lack of data to develop the group thermal comfort model
Solution: Transfer learning
  A machine learning technique that transfers previously learned knowledge to a new task [1]
  A solution for insufficient data problem [2, 3]
  Transfer the knowledge from source domain to target domain
[1] Pan, W., E. Xiang, and Q. Yang. Transfer learning in collaborative filtering with uncertain ratings. in Proceedings of the AAAI Conference on Artificial Intelligence. 2012.
[2] Gupta, N. and A.S. Jalal, Traditional to transfer learning progression on scene text detection and recognition: a survey. Artificial Intelligence Review, 2022: p. 1-46.
[3] Di, S., et al., Cross-domain traffic scene understanding: A dense correspondence-based transfer learning approach. IEEE transactions on intelligent transportation systems, 2017. 19(3): p. 745-757.

## Slide 30: Task 3.1 Transfer Learning Framework Development
Categorization of TL
  Instance-based
    Transfer the knowledge by re-sampling source instances to minimize the difference in marginal distributions
    This method is used in this study
  Feature-based
    Minimize the mismatch by transferring features to another space
    This method is not used because the features of the group thermal comfort model are typical available
  Model-based
    Keep parts of the model from source domain, and fine-tune the model for the target domain
    This method is not used because the group thermal comfort RF model is hard to fine-tune
The schema of three categories of TL [1]
[1] Asgarian, A., An Introduction to Transfer Learning, a simple and concise explanation with real examples, in Medium. 2018.

## Slide 31: Task 3.1 Transfer Learning Framework Development
The key procedure in instance-based transfer learning is sample adaptation
Sample adaptation
  Minimize the difference of marginal distributions between two domains.
  The difference is measured by Maximum Mean Discrepancy (MMD) [1]
  Use optimization method to minimize MMD
    Objective function
    Optimization algorithm: Genetic algorithm
Where:
xi and yi is the data in two distribution X and Y, respectively
K is Gaussian kernel function
σ is the parameter in K, typically equal to 1
Where:
Ds and Dt are the instances in the source and target domain
x is an indicator of the instances resampled from the source domain
[1] Xiao, D., et al., Domain adaptive motor fault diagnosis using deep transfer learning. Ieee Access, 2019. 7: p. 80937-80949

## Slide 32: Task 3.1 Transfer Learning Framework Development
Instance-based TL
  Use TL to find data from virtual testbed simulated data that is close to realistic data to enrich the training data of group thermal comfort model
Framework of model development using instance-based transfer learning
Virtual testbed
Source domain
(simulated occupant data)
Target domain
(real occupant data)
Reality
transfer

## Slide 33: Task 3.2 Evaluation Scenarios Design
Source domain: virtual testbed simulation data
  The source domain data includes 3 different numbers of occupant (5, 10, and 15)
    Design based on the zone area and the minimum area per occupant
  24 groups of each population size (thermal acceptability is sampled by RP-884)
    Make sure that the source domain have enough groups with different thermal preferences
  1-month simulation with random setpoint (65°F ~85°F)
24 groups
……
5-occupants group
……
24 groups
10-occupants group
……
24 groups
15-occupants group
Source domain data diagram

## Slide 34: Task 3.2 Evaluation Scenarios Design
Target domain scenarios design: “real data” obtained by using virtual testbed to represent the real building
  Evaluate the scenarios with different number of occupants:
  Evaluate the scenarios with different group thermal preferences
5-occupants scenario
(minimum occupant size in source domain)
15-occupants scenario
(maximum occupant size in source domain)
7-occupants scenario
(a different size not included in the source domain)
Neutral group thermal preference
(Acceptability is sampled by RP-884)
Cold group thermal preference
(manually generated acceptability)
Warm group thermal preference
(manually generated acceptability)

## Slide 35: Task 3.2 Evaluation Scenarios Design
Target domain scenarios design: “real data” obtained by using virtual testbed to represent the real building
  Evaluate the scenarios with different operational strategies
  Evaluate the scenarios with different data collection period: 1-day, 2-days, 3-days, 4-days, and 5-days
One cooling setpoint scenario
(78℉)
Three cooling setpoints scenario
(Load shifting strategy [1]: precooling: 76 ℉; normal: 78 ℉; and peak: 80 ℉)
[1] Chen, Z., et al., Development of a Hardware-in-the-loop Testbed for Laboratory Performance Verification of Flexible Building Equipment in Typical Commercial Buildings., 2023.

## Slide 36: Task 3.2 Evaluation Scenarios Design
 | Source domain | Target domain |  |  |  |  |  |  | 
Location and weather | Atlanta Summer |  |  |  |  |  |  |  | 
Building and HVAC system | Virtual testbed | “Real building” represented by virtual testbed |  |  |  |  |  |  | 
Occupants | 24 groups of 5 occupants 24 groups of 10 occupants 24 groups of 15 occupants | 5 occupants |  | 7 occupants |  |  |  | 15 occupants | 
 |  | Neutral preference |  | Cold preference |  |  |  | Warm preference | 
HVAC operation | Random cooling setpoints | One cooling setpoint |  |  |  | Three cooling setpoints |  |  | 
Data collection period | 1 month | 1 day | 2 days |  | 3 days |  | 4 days |  | 5 days
Summary of TL evaluation scenarios design
  Totally, there are 90 evaluation cases are designed.
  The source domain data remains identical, while the difference is in target domain scenarios.

## Slide 37: Task 3.2 Evaluation Scenarios Design
Evaluation method
  Develop the group thermal comfort model with and without TL, respectively
  Use target evaluation data to evaluate the model performance
    Target evaluation data generation:
      5-days data with random setpoint (72°F ~80°F [1])
  Compare the JSDnoTL_eva and JSDTL_eva
[1] ANSI/ASHRAE Standard 55-2020, Thermal Environmental Conditions for Human Occupancy, 2020
TL evaluation framework

## Slide 38: Task 3.3 Evaluation Results Analyze
Evaluation results
  Use 7-occupant scenarios as an example
Conclusion
  Effectiveness of TL
    TL always improves model predictive performance, regardless of group characteristics, HVAC system control strategies, or data collection periods
    Demonstrates strong applicability
  Impact of control strategy and data collection period on model performance
    For one-setpoint control, additional data is useless
    For three-setpoints control, additional data can improve model performance
    → The richness (information entropy [1]) of target domain data may impact model predictive performance and transfer learning effect
[1] Kozak, J. and P. Juszczuk, Entropy in Real-World Datasets and Its Impact on Machine Learning. 2023: MDPI-Multidisciplinary Digital Publishing Institute.

## Slide 39: Task 3.3 Evaluation Results Analyze
Evaluation of the impact of information entropy on:
  Model predictive performance (JSDnoTL-eva or JSDTL-eva))
  TL effect (ΔJSD = JSDnoTL-eva - JSDTL-eva))
Conclusion
  Model performance
    Higher information entropy generally results in a model with lower JSD, indicating better predictive performance
  TL effect
    All positive impact
    No significant relationship between information entropy and ΔJSD
  → TL always can enhance the model's predictive performance. However, the extent of improvement is different case by case

## Slide 40: Conclusions of Objective 3
Objective 3: TL Used in Group Occupant Thermal Comfort Model
A framework of instance-based TL is developed (task 3.1)
A series of evaluation cases are designed (task 3.2), including the difference in:
  Group occupant
  HVAC system control strategy
  Data collection period
Based on the evaluation results, TL has strong applicability in improving group thermal comfort model’s predictive performance (task 3.3)

## Slide 41
Objective 4: Development and Evaluation of Transferable MPC-based Group Occupant Centric Control (TMPC-GOCC)
Task 4.1 MPC Framework Development
Task 4.2 Evaluation Cases Design
Task 4.3 Evaluation Results Analyze

## Slide 42: Task 4.1 MPC Framework Development
Objective function:
Where:
is prediction timestep, 15 min; PH is prediction horizon, 4;
x is the control variable, i.e., HVAC system speed mode;
Optimization algorithm: Exhaustive method
[1] ANSI/ASHRAE Standard 55-2020, Thermal Environmental Conditions for Human Occupancy, 2020

## Slide 43: Task 4.1 MPC Framework Development
To demonstrate the effectiveness of the proposed TMPC-GOCC, three types of MPC are developed for comparison
  Temperature-Based MPC
    Constraint: [1]
  GOCC-Based MPC
    The group thermal comfort model is trained without TL
    Constraint:
  GOCC+TL MPC (i.e., TMPC-GOCC)
    The group thermal comfort model is trained with TL
    Constraint:
[1] ANSI/ASHRAE Standard 55-2020, Thermal Environmental Conditions for Human Occupancy, 2020

## Slide 44: Task 4.2 Evaluation Cases Design
Goal of evaluation:
  Evaluate the control performance of three MPCs
  Investigate the impact of group thermal comfort model accuracy on MPC control performance
Solution:
  Based on the TL evaluation results, 10 cases (JSDTL-eva< 0.3) were selected
  For each evaluation case
    Three types of MPC are developed
    5-day simulation using virtual testbed
  Compare the control performance in occupant comfort
Evaluation cases | JSDnoTL-eva | JSDTL-eva
5occ-N-3SP-5D | 0.326 | 0.031
15occ-N-3SP-5D | 0.221 | 0.041
7occ-N-3SP-5D | 0.323 | 0.102
15occ-N-3SP-4D | 0.276 | 0.119
5occ-N-3SP-4D | 0.408 | 0.135
15occ-N-3SP-1D | 0.413 | 0.185
15occ-N-3SP-3D | 0.363 | 0.198
7occ-N-3SP-3D | 0.448 | 0.229
5occ-C-3SP-5D | 0.367 | 0.266
7occ-N-3SP-2D | 0.496 | 0.296
TMPC-GOCC evaluation cases

## Slide 45: Task 4.2 Evaluation Cases Design
MPC evaluation index
Evaluation Index |  | Equation
Prediction accuracy | Zone air temperature | 
 | Zone air relative humidity | 
 | HVAC system power | 
 | Group occupant thermal comfort | 
Control performance | Average occupant discomfort vote | 
 | Total energy use | 
Evaluation Index |  | Equation
Prediction accuracy | Zone air temperature | 
 | Zone air relative humidity | 
 | HVAC system power | 
 | Group occupant thermal comfort | 
Control performance | Average occupant discomfort vote | 
 | Total energy use | 
Note: Since the stochastic nature of occupant thermal comfort, the occupant comfort model conducted 50 simulations for each evaluation case to capture the distribution of occupant thermal comfort votes. Therefore, the mean and median values of and are calculated.

## Slide 46: Task 4.3 Evaluation Results Analyze
The temperature-based MPC simulation results in15occ-N-3SP-4D evaluation case
Zone air temperature
Zone air relative humidity
HVAC system power
KPI |  | Result
Prediction accuracy | RMSE(Tz) | 0.26 ℃
 | RMSE(RHz) | 1.56 %
 | RMSE(Power) | 14.5 W
 |  | NaN
 |  | NaN
Control performance |  | 18.1
 |  | 18
 |  | 75.4 kWh
KPI |  | Result
Prediction accuracy | RMSE(Tz) | 0.26 ℃
 | RMSE(RHz) | 1.56 %
 | RMSE(Power) | 14.5 W
 |  | NaN
 |  | NaN
Control performance |  | 18.1
 |  | 18
 |  | 75.4 kWh

## Slide 47: Task 4.3 Evaluation Results Analyze
KPI |  | Result
Prediction accuracy | RMSE(Tz) | 0.26 ℃
 | RMSE(RHz) | 1.88 %
 | RMSE(Power) | 11.8 W
 |  | 0.285
 |  | 0.316
Control performance |  | 83.3
 |  | 90.5
 |  | 28.1 kWh
KPI |  | Result
Prediction accuracy | RMSE(Tz) | 0.26 ℃
 | RMSE(RHz) | 1.88 %
 | RMSE(Power) | 11.8 W
 |  | 0.285
 |  | 0.316
Control performance |  | 83.3
 |  | 90.5
 |  | 28.1 kWh
The GOCC-based MPC simulation results in15occ-N-3SP-4D evaluation case
Zone air temperature
Zone air relative humidity
HVAC system power

## Slide 48: Task 4.3 Evaluation Results Analyze
The GOCC+TL MPC simulation results in15occ-N-3SP-4D evaluation case
KPI |  | Result
Prediction accuracy | RMSE(Tz) | 0.33 ℃
 | RMSE(RHz) | 3.23 %
 | RMSE(Power) | 33.2 W
 |  | 0.138
 |  | 0.112
Control performance |  | 9.1
 |  | 7.5
 |  | 62.4 kWh
KPI |  | Result
Prediction accuracy | RMSE(Tz) | 0.33 ℃
 | RMSE(RHz) | 3.23 %
 | RMSE(Power) | 33.2 W
 |  | 0.138
 |  | 0.112
Control performance |  | 9.1
 |  | 7.5
 |  | 62.4 kWh
Zone air temperature
Zone air relative humidity
HVAC system power

## Slide 49: Task 4.3 Evaluation Results Analyze
Summary of the simulation results of 15occ-N-3SP-4D evaluation case
Prediction accuracy
  For zone air temperature, zone air relative humidity, and HVAC system power model
    The RMSE are all within the criteria
    (0.5 °C, 5%, and 90W) [1]
  For group thermal comfort model,
Control performance
  For group thermal comfort, 𝐴𝑣𝑔𝐷𝑖𝑠𝐶𝑜𝑚𝑓
  For HVAC system energy
[1] American Society of Heating, V., and Air Conditioning Engineers (ASHRAE), Guideline 14-2014, in Measurement of Energy and Demand Savings. 2014.

## Slide 50: Task 4.3 Evaluation Results Analyze
Overall discussion
  For occupant thermal comfort improvement
    Poor accuracy in group thermal comfort model → Incorrect MPC’s prediction → Turn off HVAC system → Higher occupant discomfort vote
    Good accuracy in group thermal comfort model → Correct MPC’s prediction → Reasonable system control → Less occupant discomfort vote
  For energy saving
    For the effective GOCC+TL MPC, energy saving depends on the group thermal preference
    The effective GOCC+TL MPC can identify a suitable zone air temperature setpoint, and determine energy savings by comparison with the baseline.

## Slide 51: Task 4.3 Evaluation Results Analyze
Group thermal comfort model JSD threshold
  Investigate the relationship between group thermal comfort model’s JSD and occupant comfort improvement in GOCC+TL MPC
    Occupant comfort improvement ()
The JSD threshold is inferred after quadratic curve fitting
  Deduction: if JSD < 0.2, the proposed TMPC-GOCC strategy is expected to improve group occupant comfort
  As a recommended criteria for group thermal comfort model development
Notes: I just mentioned that the key of the proposed MPC success or not is the accuracy of the group thermal comfort model. So, in this slide, I want to find out the JSD threshold.
What I did is investigating the relationship between group thermal comfort model’s JSD and occupant comfort improvement in the MPC. The occupant comfort improvement can be called 𝛥𝐴𝑣𝑔𝐷𝑖𝑠𝑐𝑜𝑚𝑓𝑉𝑜𝑡𝑒, which is calculated based on the discomfort vote in the temperature-based MPC and the GOCC+TL MPC.
And then I can make the plot of the model JSD and 𝛥𝐴𝑣𝑔𝐷𝑖𝑠𝑐𝑜𝑚𝑓𝑉𝑜𝑡𝑒. The blue dot is the result coming from the mean value, the orange dot is coming from the median value. And I make a quadratic curve fitting for those dot. For comparison purpose, I also make a dashed line for 𝛥𝐴𝑣𝑔𝐷𝑖𝑠𝑐𝑜𝑚𝑓𝑉𝑜𝑡𝑒=0.
Based on the plot, we can make a deduction that, if model’s JSD is less than 0.212, the proposed TMPC-GOCC strategy is expected to improve group occupant comfort. This threshold can be a recommended criteria for the group thermal comfort mode development for the new task in the future.

## Slide 52: Conclusions of Objective 4
Objective 4: Development and Evaluation of TMPC-GOCC
A framework of TMPC-GOCC is developed (task 4.1)
Three types of the MPC are designed for comparison (task 4.2)
  Temperature-based MPC
  GOCC-based MPC
  GOCC+TL MPC (i.e., TMPC-GOCC)
Evaluation results demonstrate the advantages of the proposed TMPC-GOCC strategy in improving group thermal comfort. And the threshold of group thermal comfort model accuracy is determined (task 4.3)

## Slide 53: Overall conclusion and future work
Conclusions
Future Works
Objective 1: Virtual Testbed Development
A virtual testbed, including ASHP, single zone, and occupant, is developed
Explore more evaluation scenarios by developing different testbeds
Objective 2: Predictive Model Development
Prediction models used in MPC are developed, including group thermal comfort model, zone environment model, and HVAC system power model
Explore category classification for group thermal comfort model in large-population cases
Objective 3: Transfer Learning Used in Group Thermal Comfort Model
The TL has strong applicability in improving predictive performance of the group thermal comfort model
Explore the optimization algorithm used in sample adaptation
Explore the effectiveness in more scenarios
Objective 4: TMPC-GOCC Development and Evaluation
TMPC-GOCC can improve occupant comfort when the group thermal comfort model is accurate
Explore an indicator to integrate building energy and occupant thermal comfort

## Slide 54: Publication
Published Journal Papers
Li Y, Chen Z, Wen J, et al. A framework for calibrating and validating an HVAC system in Modelica[J]. Journal of Building Performance Simulation, 2025: 1-21.
Kimball R., Wen J., O’Neill Z., Li Y., et al. Developing Learning-Based Models for Occupant Centric Control[J]. 2022.
Calfa C, Yang Z, Li Y, et al. Performance assessment of a real water source heat pump within a hardware-in-the-loop (HIL) testing environment[J]. Science and Technology for the Built Environment, 2023, 29(10): 1011-1026.
Chen Z, Wen J, Li Y, et al. Advanced co-simulation framework for assessing the interplay between occupant behaviors and demand flexibility in commercial buildings[J]. Science and Technology for the Built Environment, 2024, 30(9): 1094-1113.
Published Conference Papers
Li Y., Chen Z, Wen J, et al. A framework for calibrating and validating an air loop dynamic model in an HVAC system in Modelica[C]. Proceedings of Building Simulation 2023: 18th Conference of IBPSA, Shanghai, CN, 2023.
Chen, Z., Wen, J., Li Y., et al., “A hardware-in-the-loop approach for laboratory performance verification of flexible building equipment in a typical commercial building”, ASHRAE Annual Conference, June 2021.
Chen, Z., Wen, J., Bushby, S. T., Lo, L. J., O’Neill, Z., Payne, W. V., Li Y., et al., “Development of a hardware-in-the-loop testbed for laboratory performance verification of flexible building equipment in typical commercial buildings”, ASHRAE Annual Conference, June 2022, Toronto, Ontario Canada.
Calfa, C., Yang, Z., Fu, Y., Chen, Z., O’Neill, Z., Wen, J., Li Y., et al., “Development of a water source heat pump hardware-in-the-loop (HIL) testing facility for smart building applications”, ASHRAE Annual Conference, June 2022, Toronto, Ontario Canada.
Chen, Z., Wen, J., Bushby, S. T., Lo, L. J., O’Neill, Z., Payne, W. V., Li Y, et al., “An analysis of the hybrid internal mass modeling approach in EnergyPlus”, eSim 2022 Conference, June 2022, Ottawa, ON.
Chen Z, Li Y, Wen J, et al. A simulation framework for analyzing the impact of stochastic occupant behaviors on demand flexibility in typical commercial buildings[C]//ASHRAE 2023 annual conference. 2023.
Calfa C., Yang Z., Li Y., et al. Performance Assessment of a Model Predictive Controller for a Heat Pump in a Hardware-in-the-Loop Experimental Test Environment. ASHRAE 2025 winter conference, Orlando, Florida, February 8-12, 2025.

## Slide 55: Publication
Future publication plan
Li Y, Chen Z, Wen J. A framework of transfer learning used in group occupant thermal comfort model
Li Y, Chen Z, Wen J. Development of an MPC-based OCC with consideration of group occupant thermal comfort

## Slide 56
Thank You
Yicheng Li
Building Science and Engineering Group (BSEG) | Drexel University
yl3328@drexel.edu

## Slide 57
Backup

## Slide 58: HVAC System Model: ASHP
Modeling method
  System performance
    Power and capacity curve is related to
      zone air temperature
      zone air dewpoint temperature
      outdoor air temperature
    The curve is obtained by quadratic curve fitting using experimental data
    Back-calculate the supply air condition based on the return air condition and the system capacity
  Controller

## Slide 59: Occupant Comfort model

## Slide 60: Task 1.1 HVAC System Model
Model development
  Model I/O
    Input: zone and outdoor air condition, zone temperature setpoint (system speed mode)
    Output: supply air condition and system power
  Modelling method
    Use second-order polynomial regression method and pervious experiment data [1, 2] to fit the system performance curve
  Error
    The CVRMSE in model outputs are all less than 5%.
[1] Payne, W.V., S.H. Yoon, and P.A. Domanski, Heating mode performance measurements for a residential heat pump with single-faults imposed. 2017: US Department of Commerce, National Institute of Standards and Technology.
[2] Jin Wen, Z.C., et al., (2023), Hardware-in-the-loop Laboratory Performance Verification of Flexible Building Equipment in a Typical Commercial Building: Performance of Heating, Ventilation, and Air Conditioning and Thermal Energy Storage Across the United States, National Institute of Standards and Technology, https://doi.org/10.18434/mds2-3058
ASHP schematic [1]
HVAC system description
  A two-stage Air Source Heat Pump (ASHP) at National Institute of Standards and Technology [1]

## Slide 61: Task 1.2 Zone Model
Zone model description
  A typical small office EnergyPlus model from the Commercial Prototype Building Models [1]
  A south-facing room was chosen as the simulated zone.
Model adaptation
  Export as a Functional Mockup Unit (FMU) [2]
  Model I/O
    Input: supply air condition
    Output: zone air condition
[1] U. S. DOE. Commercial Prototype Building Models. Available: https://www.energycodes.gov/development/commercial/prototype_models
[2] EnergyPlusToFMU, L.B.N. Laboratory, Editor. 2109, Lawrence Berkeley National Laboratory: https://simulationresearch.lbl.gov/.
Small office floor plan

## Slide 62: Task 1.3 Occupant Thermal Comfort Model
Original model description
  Agent-based model for occupant’s comfort and behaviors [1]
    Initialize virtual occupants with personal characteristics
      Thermal acceptability range
      Behavior constraint
    Based on environmental conditions, stochastically simulate:
      Occupant’s thermal sensation and comfort
      Occupant’s behavior
Model adaptation
  Simulate occupant thermal comfort only
  Model I/O
    Input: zone air condition
    Output: occupant’s comfort vote
[1] Langevin, J., J. Wen, and P.L. Gurian, Modeling thermal comfort holistically: Bayesian estimation of thermal sensation, acceptability, and preference distributions for office building occupants. Building and Environment, 2013. 69: p. 206-226
Diagram of the agent-based occupant model [1]

## Slide 63: Group thermal comfort model
Model evaluation
  Goal:
    Trying to ensure that the model prediction can have a close probability distributions compared with the real value under different environments.
    Considering follow-up transfer learning, the similarity of the two probability distributions needs to be quantified to evaluate the performance of transfer learning.
  Method: 5-fold cross-validation
  Typical method to evaluate the performance of a classification model:
    Instance-based: confusion matrix (includes accuracy, precision, recall, F1 score, ROC-AUC…)
    Probability-based:
      Statistical test: T test, K-S test, Chi-Square test
      Similarity measures: Jensen-Shannon Divergence (JSD), Earth Mover's Distance (EMD), logistic loss
Similarity measurement
Differential method
Probability-based method

## Slide 64: JSD Calculation
Error evaluation
  Process
    Divide the entire feature space into several subspaces
      0.5 C for the feature related to temperature [1]
      5% for the feature related to relative humidity
    Calculate the JSD in each subspace
    Calculate the weighted average JSD
[1] Battistel, L., et al., An investigation on humans’ sensitivity to environmental temperature. Scientific Reports, 2023. 13(1): p. 21353.
Weighted mean JSD calculation schema
Where:
P and Q: p(x) and q(x), the two probability distributions in sample space X;
n is the number of sample in the space.

## Slide 65: The smallest RH difference
In typical office condition
Air temperature=26 C
Air speed=0.1 m/s
Mean radiant temperature=28C
Clothing level=0.6 clo
Metabolic rate =1.2 met
For every 4% increase in humidity, the PPD increases by 1%
PMV vs RHz
PPD vs RHz

## Slide 66: Active Learning

## Slide 67: Model Prediction Error
Candidate learning algorithms | Candidate Prediction Horizons |  |  | 
 | ph=1 | ph=2 | ph=4 | ph=8
ANN | 0.35 | 0.48 | 0.72 | 1.12
RNN | 0.08 | 0.13 | 0.21 | 0.28
MLR | 1.31 | 1.54 | 2.06 | 3.12
MARS | 0.12 | 0.85 | 1.97 | 2.64
Zone air temperature prediction error (RMSE) [°C]
Candidate learning algorithms | Candidate Prediction Horizons |  |  | 
 | ph=1 | ph=2 | ph=4 | ph=8
ANN | 1.48 | 3.26 | 5.73 | 8.59
RNN | 3.47 | 5.82 | 8.36 | 11.09
MLR | 5.63 | 9.27 | 13.58 | 18.94
MARS | 1.51 | 2.74 | 4.74 | 8.12
Zone air relative humidity prediction error (RMSE) [%]
Candidate learning algorithms | Candidate Prediction Horizons |  |  | 
 | ph=1 | ph=2 | ph=4 | ph=8
ANN | 62 | 65 | 71 | 79
RNN | 62 | 74 | 86 | 98
MLR | 81 | 95 | 122 | 148
MARS | 64 | 69 | 75 | 88
HVAC system power prediction error (RMSE) [W]

## Slide 68: Model Prediction Error

## Slide 69: Task 2.2 Zone Environment and HVAC System Power Model Development
Validation goal
  Determine model structure
  Determine the prediction horizon for MPC
Validation index
  Root Mean Square Error (RMSE)
Validation results
  PH selection
    PH=4, based on the typical criteria (0.5 °C for temperature, 5% for relative humidity, and 90W for HVAC system power [1])
  Model structures selection and error
    Zone air temperature RNN model: 0.21 °C
    Zone air relative humidity MARS model: 4.74%
    HVAC system power ANN model: 71W
[1] American Society of Heating, V., and Air Conditioning Engineers (ASHRAE), Guideline 14-2014, in Measurement of Energy and Demand Savings. 2014.
Notes: After comparing the validation error of the model developed by different model structures, the suitable model structures can be selected.
Another thing needed to be determined is the prediction horizon. Because at the end, this study will develop an MPC strategy, which involves the prediction in multiple step. So, how long the prediction horizon can be also need to de determined.
The validation index is Root Mean Square Error.
And after checking the validation results, based on the criteria on Guideline 14, I select that the PH=4.
As for the model structures, the zone air temperature use RNN model, zone air relative humidity model use MARS model, and the HVAC system model use ANN model. The error of each model is also provided. They are all with in the criteria.

## Slide 70: Task 3.2 Evaluation Scenarios Design
Goal:
  Evaluate the feasibility of the proposed TL framework
Method:
  Design different scenarios to determine whether the TL are effective
    Source domain design
      Source domain data is the simulation data from virtual testbed
      One super-rich dataset covers a wide range of environmental conditions and occupant profiles
    Target domain design
      Target domain data is the “real data” obtained by using virtual testbed to represent the real building
      Design different scenarios to mimic the data that could be collected in real life

## Slide 71: Task 3.2 Evaluation Scenarios Design
The source domain data contains 3 different numbers of people (5, 10, and 15)
  Zone area = 113 m²
  Minimum area per occupant = 7.4 m² [1]
24 groups of each population size (thermal acceptability is sampled by RP-884)
  The chi-square test [2] is used to determine the goodness-of-fit of two distributions (PMV-PDD curve in RP-884 and the curve in source domain)
  Criteria: p-value =0.95
1-month simulation with random setpoint (65°F ~85°F)
[1] Voss, J., Revisiting office space Standards. Grand Rapids, MI: Haworth, 2000: p. 1-6

## Slide 72: Chi-square Test
Method: A typical method to test the goodness-of-fit of two distributions is the chi-square test [1].
+
Where:
and are the number of observation in category 𝑖 in distribution 1 and 2, respectively.
, , and are the number of samples in distribution 1, 2, and total, respectively.
and are the expected counts of observation 𝑖 in the distribution 1 and 2, respectively.
is the number of the category, which is 7 in this study (PMV=-3:3).
, , and are the chi-square test statistic of distribution 1, 2, and total.
Based on and the degrees of freedom (7-1=6) , a p-value can be calculated. Typically:
If the p-value < 0.05, the two distributions can be considered significantly different.
If the p-value > 0.95, the two distributions can be considered similar.
[1] Abramowitz, Milton, and Irene A. Stegun, eds. Handbook of Mathematical Functions: With Formulas, Graphs, and Mathematical Tables. 9. Dover print.; [Nachdr. der Ausg. von 1972]. Dover Books on Mathematics. New York, NY: Dover Publ, 2013.

## Slide 73: Information Entropy
Information entropy varies with the time period of data collection
Where:
is the feature and outcome matrix
is the eigenvector
is the normalized eigenvalue
is the information (eigen) entropy

## Slide 74
TL evaluation results

## Slide 75: Task 4.1 MPC Framework Development
Flowchart of the development process of the three MPCs
Three types of MPC
  Temperature-Based MPC
  GOCC-Based MPC
    The group thermal comfort model is trained without transfer learning
  GOCC+TL MPC (TMPC-GOCC)
    The group thermal comfort model is trained with transfer learning

## Slide 76: Task 4.1 MPC Framework Development
Objective function:
Where:
is prediction timestep, 15 min; PH is prediction horizon, 4;
x is the control variable, i.e., HVAC system speed mode;
Optimization algorithm: Exhaustive method
[1] ANSI/ASHRAE Standard 55-2020, Thermal Environmental Conditions for Human Occupancy, 2020

## Slide 77: MPC Model Predictive Error
 | 5occ-N-3SP-5D |  |  | 15occ-N-3SP-5D |  |  | 7occ-N-3SP-5D |  |  | 15occ-N-3SP-4D |  |  | 5occ-N-3SP-4D |  | 
 | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W]
Temperature-based | 0.2 | 1.51 | 24.5 | 0.26 | 1.56 | 14.5 | 0.09 | 0.16 | 21.1 | 0.26 | 1.56 | 14.5 | 0.2 | 1.51 | 24.5
GOCC-based | 0.21 | 2.86 | 5.5 | 0.4 | 1.52 | 43.5 | 0.41 | 1.16 | 31 | 0.26 | 1.88 | 11.8 | 0.33 | 4.42 | 37.3
GOCC+TL | 0.24 | 1.71 | 17 | 0.28 | 1.67 | 20.5 | 0.21 | 2.61 | 5.2 | 0.33 | 3.23 | 33.2 | 0.36 | 4.21 | 47.9
 | 15occ-N-3SP-1D |  |  | 15occ-N-3SP-3D |  |  | 7occ-N-3SP-3D |  |  | 5occ-C-3SP-5D |  |  | 7occ-N-3SP-2D |  | 
 | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W] | Tz [C] | RHz [%] | power [W]
Temperature-based | 0.26 | 1.56 | 14.5 | 0.26 | 1.56 | 14.5 | 0.09 | 0.16 | 21.1 | 0.2 | 1.51 | 24.5 | 0.09 | 0.16 | 21.1
GOCC-based | 0.26 | 1.2 | 16.4 | 0.28 | 3.03 | 20.7 | 0.43 | 2.69 | 44.2 | 0.44 | 2.66 | 15.7 | 0.23 | 2.68 | 6.8
GOCC+TL | 0.37 | 2.53 | 23.7 | 0.29 | 2.95 | 22.8 | 0.27 | 1.58 | 25 | 0.25 | 1.63 | 12.5 | 0.36 | 3.11 | 29.5
    Criteria: 0.5 °C, 5%, and 90W [1]
[1] American Society of Heating, V., and Air Conditioning Engineers (ASHRAE), Guideline 14-2014, in Measurement of Energy and Demand Savings. 2014.

## Slide 78: MPC Evaluation Result of JSD

## Slide 79: Occupant Average Discomfort Vote

## Slide 80: Energy Use

## Slide 81: Group Thermal Comfort MPC Predicted Results vs Testbed Simulation Results
b) 15occ-N-3SP-4D GOCC-based MPC case simulated group thermal comfort
a) 15occ-N-3SP-4D GOCC-based MPC case MPC predicted group thermal comfort
a) 15occ-N-3SP-4D GOCC+TL MPC case MPC predicted group thermal comfort
b) 15occ-N-3SP-4D GOCC+TL MPC case simulated group thermal comfort
GOCC-based MPC case
GOCC+TL MPC case
MPC predicted
MPC predicted
MPC predicted
Real
Real

## Slide 82: Group Occupant thermal Preference

## Slide 83: JSD Threshold